## Sheet1
AIRFOIL BLADE
SIZE S - AF - 22 | [6 empty] | SINGLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | SINGLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 22¼inches 565 mm | [13 empty] | SIZE 22 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel circumference 5.83 feet 1.777 m | [13 empty] | CLASS I |  | 1962
Inlet Diameter / Area 24 3/16 inches Dia/3.14 sq f.t 614mm /.2917 m² | [13 empty] | CLASS II |  | 2560
Outlet Size Area 23 5/16 *17 7/16Inches I.D/2.82sq.ft 592*443mm/.2620 m² | [13 empty] | CLASS III |  | 3226
Tip Speed 5.83 * rpm ft./minute 1.777*RPM m/minute | [13 empty] | CLASS IV |  | 3549
Maximum BHP 1.15*(RPM÷1000)³ BHP .8576 * (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
1692 | 600 | 451 | 0.1 | 505 | 0.14 | 556 | 0.18 | 603 | 0.22
1974 | 700 | 489 | 0.13 | 540 | 0.17 | 585 | 0.22 | 629 | 0.27 | 672 | 0.32 | 711 | 0.37
2256 | 800 | 531 | 0.16 | 576 | 0.21 | 620 | 0.26 | 660 | 0.32 | 698 | 0.37 | 737 | 0.43 | 773 | 0.48 | 843 | 0.6
2538 | 900 | 573 | 0.2 | 616 | 0.25 | 656 | 0.31 | 695 | 0.37 | 731 | 0.43 | 765 | 0.49 | 800 | 0.56 | 866 | 0.68 | 927 | 0.8
2820 | 1000 | 617 | 0.24 | 658 | 0.3 | 696 | 0.37 | 731 | 0.43 | 767 | 0.5 | 800 | 0.56 | 831 | 0.63 | 892 | 0.77 | 952 | 0.91 | 1008 | 1.05
3102 | 1100 | 661 | 0.29 | 701 | 0.36 | 737 | 0.43 | 770 | 0.5 | 802 | 0.57 | 835 | 0.64 | 866 | 0.72 | 923 | 0.87 | 978 | 1.02 | 1034 | 1.17
3384 | 1200 | 707 | 0.34 | 745 | 0.42 | 779 | 0.5 | 812 | 0.57 | 842 | 0.65 | 871 | 0.73 | 901 | 0.81 | 957 | 0.97 | 1009 | 1.13 | 1060 | 1.3
3666 | 1300 | 753 | 0.41 | 789 | 0.49 | 822 | 0.58 | 854 | 0.66 | 883 | 0.74 | 911 | 0.82 | 937 | 0.91 | 993 | 1.08 | 1043 | 1.25 | 1091 | 1.43
3948 | 1400 | 799 | 0.48 | 834 | 0.57 | 866 | 0.66 | 896 | 0.75 | 925 | 0.84 | 952 | 0.93 | 978 | 1.02 | 1028 | 1.2 | 1079 | 1.38 | 1125 | 1.57
4230 | 1500 | 846 | 0.57 | 879 | 0.66 | 910 | 0.75 | 940 | 0.85 | 967 | 0.95 | 994 | 1.04 | 1019 | 1.14 | 1066 | 1.33 | 1114 | 1.53 | 1161 | 1.73
4512 | 1600 | 874 | 0.66 | 926 | 0.76 | 955 | 0.86 | 984 | 0.96 | 1010 | 1.07 | 1036 | 1.17 | 1061 | 1.27 | 1107 | 1.47 | 1151 | 1.68 | 1196 | 1.89
4794 | 1700 | 942 | 0.77 | 972 | 0.87 | 1001 | 0.98 | 1028 | 1.08 | 1054 | 1.19 | 1079 | 1.3 | 1103 | 1.41 | 1148 | 1.63 | 1191 | 1.84 | 1232 | 2.07
5076 | 1800 | 990 | 0.88 | 1019 | 0.99 | 1047 | 1.1 | 1073 | 1.22 | 1098 | 1.33 | 1123 | 1.45 | 1146 | 1.57 | 1190 | 1.79 | 1232 | 2.02 | 1272 | 2.25
5358 | 1900 | 1039 | 1.01 | 1066 | 1.13 | 1093 | 1.24 | 1118 | 1.36 | 1143 | 1.48 | 1167 | 1 | 1189 | 1.73 | 1233 | 1.97 | 1274 | 2.21 | 1312 | 2.45
5640 | 2000 | 1088 | 1.15 | 1114 | 1.28 | 1140 | 1.4 | 1164 | 1.52 | 1188 | 1.65 | 1211 | 1.77 | 1233 | 1.9 | 1276 | 2.16 | 1316 | 2.42 | 1354 | 2.67
6204 | 2200 | 1187 | 1.47 | 1211 | 1.61 | 1234 | 1.75 | 1257 | 1.88 | 1280 | 2.02 | 1301 | 2.16 | 1322 | 2.29 | 1363 | 2.58 | 1401 | 2.86 | 1438 | 3.14
6768 | 2400 | 1286 | 1.85 | 1308 | 2 | 1330 | 2.16 | 1351 | 2.31 | 1372 | 2.45 | 1393 | 2.6 | 1413 | 2.75 | 1451 | 3.05 | 1488 | 3.36 | 1523 | 3.67
7332 | 2600 | 1386 | 2.3 | 1407 | 2.46 | 1427 | 2.63 | 1447 | 2.79 | 1466 | 2.95 | 1486 | 3.11 | 1505 | 3.27 | 1542 | 3.59 | 1577 | 3.92 | 1610 | 4.26
7896 | 2800 | 1487 | 2.81 | 1506 | 2.99 | 1525 | 3.17 | 1543 | 3.35 | 1562 | 3.52 | 1580 | 3.69 | 1598 | 3.86 | 1633 | 4.21 | 1667 | 4.56 | 1699 | 4.91
8460 | 3000 | 1588 | 3.4 | 1606 | 3.59 | 1623 | 3.78 | 1641 | 3.97 | 1658 | 4.17 | 1675 | 4.35 | 1692 | 4.54 | 1725 | 4.9 | 1758 | 5.27 | 1789 | 5.65
9024 | 3200 | 1689 | 4.08 | 1706 | 4.28 | 1722 | 4.48 | 1739 | 4.68 | 1755 | 4.89 | 1771 | 5.09 | 1787 | 5.29 | 1819 | 5.68 | 1850 | 6.07 | 1880 | 6.47
9588 | 3400 | 1790 | 4.83 | 1806 | 5.05 | 1822 | 5.26 | 1838 | 5.48 | 1853 | 5.69 | 1868 | 5.91 | 1883 | 6.13 | 1913 | 6.54 | 1943 | 6.96 | 1972 | 7.37
10152 | 3600 | 1892 | 5.69 | 1907 | 5.91 | 1922 | 6.13 | 1937 | 6.36 | 1951 | 6.59 | 1966 | 6.82 | 1980 | 7.05 | 2008 | 7.5 | 2034 | 7.94 | 2064 | 8.38
10716 | 3800 | 1993 | 6.63 | 2008 | 6.87 | 2022 | 7.11 | 2036 | 7.34 | 2050 | 7.58 | 2064 | 7.83 | 2078 | 8.07 | 2104 | 8.56 | 2131 | 9.02 | 2158 | 9.48
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
3666 | 1300 | 1137 | 1.61 | 1231 | 1.97 | 1316 | 2.33
3948 | 1400 | 1170 | 1.77 | 1257 | 2.15 | 1342 | 2.53 | 1421 | 2.92
4230 | 1500 | 1204 | 1.93 | 1285 | 2.34 | 1368 | 2.75 | 1446 | 3.16 | 1519 | 3.58
4512 | 1600 | 1239 | 2.1 | 1319 | 2.54 | 1394 | 2.98 | 1472 | 3.41 | 1545 | 3.85 | 1613 | 4.29 | 1683 | 4.8
4794 | 1700 | 1275 | 2.29 | 1354 | 2.74 | 1427 | 3.21 | 1498 | 3.68 | 1570 | 4.14 | 1639 | 4.6 | 1703 | 5.07 | 1767 | 5.57
5076 | 1800 | 1311 | 2.49 | 1389 | 2.96 | 1461 | 3.45 | 1528 | 3.95 | 1597 | 4.44 | 1664 | 4.92 | 1729 | 5.41 | 1790 | 5.91 | 1849 | 6.41
5358 | 1900 | 1349 | 2.7 | 1425 | 3.19 | 1496 | 3.7 | 1563 | 4.22 | 1625 | 4.75 | 1691 | 5.26 | 1755 | 5.77 | 1816 | 6.29 | 1875 | 6.81 | 1931 | 7.34
5640 | 2000 | 1390 | 2.92 | 1461 | 3.44 | 1531 | 3.97 | 1597 | 4.5 | 1659 | 5.05 | 1718 | 5.61 | 1781 | 6.15 | 1842 | 6.69 | 1900 | 7.23 | 1956 | 7.78
6204 | 2200 | 1473 | 3.42 | 1539 | 3.98 | 1603 | 4.55 | 1667 | 5.13 | 1728 | 5.71 | 1786 | 6.31 | 1842 | 6.91 | 1895 | 7.53 | 1952 | 8.12 | 2008 | 8.71
4768 | 2400 | 1557 | 3.98 | 1621 | 4.58 | 1681 | 5.2 | 1739 | 5.82 | 1799 | 6.44 | 1856 | 7.08 | 1911 | 7.72 | 1963 | 8.37 | 2013 | 9.03 | 2062 | 9.71
7332 | 2600 | 1643 | 4.59 | 1705 | 5.26 | 1763 | 5.91 | 1818 | 6.57 | 1871 | 7.25 | 1927 | 7.92 | 1981 | 8.6 | 2032 | 9.29 | 2082 | 9.99 | 2129 | 10.7
7896 | 2800 | 1730 | 5.27 | 1790 | 6 | 1847 | 6.7 | 1900 | 7.41 | 1952 | 8.12 | 2001 | 8.85 | 2052 | 9.57 | 2103 | 10.3 | 2151 | 11.03 | 2199 | 11.78
8460 | 3000 | 1819 | 6.03 | 1877 | 6.8 | 1932 | 7.59 | 1984 | 8.33 | 2034 | 9.08 | 2082 | 9.84 | 2128 | 10.62 | 2175 | 11.39 | 2223 | 12.16 | 2269 | 12.95
9024 | 3200 | 1909 | 6.87 | 1965 | 7.68 | 2018 | 8.51 | 2069 | 9.34 | 2117 | 10.13 | 2164 | 10.93 | 2209 | 11.74 | 2253 | 12.56 | 2295 | 13.39 | 2341 | 14.21
9588 | 3400 | 2000 | 7.79 | 2053 | 8.65 | 2105 | 9.52 | 2154 | 10.4 | 2202 | 11.28 | 2247 | 12.11 | 2291 | 12.96 | 2334 | 13.82 | 2375 | 14.69 | 2416 | 15.57
10152 | 3600 | 2091 | 8.82 | 2143 | 9.71 | 2193 | 10.62 | 2241 | 11.55 | 2287 | 12.48 | 2332 | 13.41 | 2375 | 14.29 | 2417 | 15.19 | 2457 | 16.099 | 2496 | 17.01
10716 | 3800 | 2184 | 9.94 | 2234 | 10.88 | 2283 | 11.83 | 2329 | 12.79 | 2374 | 13.77 | 2418 | 14.76 | 2460 | 15.73 | 2500 | 16.66 | 2540 | 17.61 | 2578 | 18.54
11280 | 4000 | 2277 | 11.17 | 2326 | 12.15 | 2373 | 13.14 | 2418 | 14.15 | 2462 | 15.16 | 2504 | 16.19 | 2545 | 17..24 | 2585 | 18.26 | 2624 | 19.24 | 2661 | 20.23
11844 | 4200 | 2371 | 12.51 | 2418 | 13.53 | 2464 | 14.57 | 2508 | 15.61 | 2550 | 16.67 | 2591 | 17.74 | 2631 | 18.84 | 2670 | 19.91 | 2708 | 20.99 | 2745 | 22.02
12408 | 4400 | 2466 | 13.97 | 2511 | 15.3 | 2555 | 16.11 | 2598 | 17.19 | 2639 | 18.29 | 2679 | 19.4 | 2719 | 20.52 | 2757 | 21.66 | 2794 | 22.8 | 2830 | 23.94
12972 | 4600 | 2561 | 15.55 | 2605 | 16.65 | 2648 | 17.77 | 2689 | 18.9 | 2729 | 20.04 | 2769 | 21.19 | 2807 | 22.35 | 2844 | 23.52 | 2880 | 24.7 | 2916 | 25.9
13536 | 4800 | 2657 | 17.24 | 2699 | 18.4 | 2741 | 19.56 | 2781 | 20.73 | 2820 | 21.91 | 2858 | 23.1 | 2896 | 24.3 | 2932 | 25.52 | 2967 | 26.74 | 3002 | 27.97
14100 | 5000 | 2754 | 19.05 | 2794 | 20.29 | 2834 | 21.49 | 2874 | 22.7 | 2912 | 23.92 | 2949 | 25.15 | 2985 | 26.39 | 3021 | 27.64 | 3055 | 28.91 | 3089 | 30.18
14664 | 5200 | 2851 | 20.99 | 2890 | 22.31 | 2929 | 23.55 | 2967 | 24.80 | 3004 | 26.07 | 3040 | 27.34 | 3075 | 28.62 | 3110 | 29.91 | 3144 | 31.21 | 3177 | 32.52
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
6204 | 2200 | 2062 | 9.3 | 2164 | 10.51 | 2260 | 11.73
6768 | 2400 | 2114 | 10.35 | 2215 | 11.64 | 2311 | 12.94 | 2402 | 14.25 | 2492 | 15.69
7332 | 2600 | 2176 | 11.42 | 2268 | 12.85 | 2363 | 14.23 | 2453 | 15.63 | 2539 | 17.05 | 2621 | 18.48 | 2707 | 20.11
7896 | 2800 | 2244 | 12.53 | 2332 | 14.06 | 2415 | 15.62 | 2505 | 17.1 | 2590 | 18.6 | 2672 | 20.11 | 751 | 21.63 | 2826 | 23.17 | 2905 | 24.92
8460 | 3000 | 2314 | 13.74 | 2400 | 15.34 | 2482 | 16.97 | 2560 | 18.64 | 2642 | 20.24 | 2723 | 21.83 | 2802 | 23.44 | 2877 | 25.06 | 2950 | 26.68 | 3020 | 28.32
9024 | 3200 | 2385 | 15.04 | 2470 | 16.71 | 2550 | 18.42 | 2627 | 20.15 | 2701 | 21.92 | 2776 | 23.67 | 2853 | 25.35 | 2928 | 27.05 | 3001 | 28.76 | 3071 | 30.48
9588 | 3400 | 2457 | 16.44 | 2540 | 18.19 | 2620 | 19.97 | 2696 | 21.78 | 2769 | 23.61 | 2839 | 25.47 | 2907 | 27.35 | 2980 | 29.15 | 3052 | 30.94 | 3122 | 32.75
10152 | 3600 | 2535 | 17.93 | 2612 | 19.78 | 2691 | 21.64 | 2766 | 23.51 | 2838 | 25.42 | 2907 | 27.35 | 2974 | 29.3 | 3039 | 31.28 | 3104 | 33.25 | 3173 | 35.13
10716 | 3800 | 2616 | 19.52 | 2689 | 21.46 | 2762 | 23.41 | 2837 | 25.36 | 2908 | 27.34 | 2976 | 29.37 | 3042 | 31.37 | 3107 | 33.41 | 3169 | 35.49 | 3229 | 37.58
11280 | 4000 | 2698 | 21.22 | 2769 | 23.24 | 2838 | 25.29 | 2908 | 27.34 | 2978 | 29.39 | 3046 | 31.46 | 3112 | 33.56 | 3175 | 35.67 | 3236 | 37.81 | 3296 | 39.98
11844 | 4200 | 2781 | 23.05 | 2851 | 25.14 | 2918 | 27.27 | 2983 | 29.42 | 3050 | 31.56 | 3117 | 33.71 | 3182 | 35.87 | 3244 | 38.06 | 3305 | 40.27 | 3364 | 42.51
12408 | 4400 | 2866 | 25.01 | 2934 | 27.18 | 3000 | 29.37 | 3063 | 31.6 | 3124 | 33.85 | 3188 | 36.09 | 3252 | 38.33 | 3314 | 40.59 | 3374 | 42.87 | 3433 | 45.17
12972 | 4600 | 2951 | 27.1 | 3018 | 29.34 | 3082 | 31.61 | 3144 | 33.91 | 3205 | 36.23 | 3263 | 38.58 | 3324 | 40.92 | 3385 | 43.25 | 3445 | 45.61 | 3503 | 47.98
13536 | 4800 | 3036 | 29.21 | 3102 | 31.65 | 3166 | 33.99 | 3227 | 36.36 | 3286 | 38.76 | 3343 | 41.18 | 3399 | 43.63 | 3457 | 46.06 | 3516 | 48.49