## Sheet1
AIRFOIL BLADE
SIZE S - AF - 27 | [6 empty] | SINGLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | SINGLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 27inches 686 mm | [13 empty] | SIZE 27 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel circumference 7.07 feet 2.155 m | [13 empty] | CLASS I |  | 1548
Inlet Diameter / Area 29 11/16 inches Dia/4.75 sq f.t 754mm /.4413 m² | [13 empty] | CLASS II |  | 2020
Outlet Size Area 28⅜*21 5/16Inches I.D/4.20 sq.ft 721*541mm/.3902 m² | [13 empty] | CLASS III |  | 2546
Tip Speed 7.07 * rpm ft./minute 2.155*RPM m/minute | [13 empty] | CLASS IV |  | 2800
Maximum BHP 3.05*(RPM÷1000)³ BHP 2.274 * (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
2520 | 600 | 356 | 0.14 | 401 | 0.19 | 446 | 0.25 | 494 | 0.32
2940 | 700 | 386 | 0.17 | 427 | 0.23 | 465 | 0.3 | 501 | 0.37 | 544 | 0.45
3360 | 800 | 418 | 0.21 | 455 | 0.28 | 490 | 0.36 | 523 | 0.43 | 556 | 0.51 | 591 | 0.59 | 627 | 0.68
3780 | 900 | 451 | 0.26 | 486 | 0.34 | 518 | 0.42 | 550 | 0.5 | 579 | 0.59 | 609 | 0.67 | 637 | 0.76 | 702 | 0.96
4200 | 1000 | 486 | 0.32 | 518 | 0.4 | 549 | 0.49 | 577 | 0.58 | 60 | 0.67 | 633 | 0.76 | 659 | 0.86 | 710 | 1.05 | 770 | 1.28 | 825 | 1.51
4620 | 1100 | 522 | 0.38 | 552 | 0.47 | 581 | 0.57 | 608 | 0.67 | 634 | 0.77 | 660 | 0.87 | 685 | 0.97 | 733 | 1.18 | 779 | 1.39 | 833 | 1.63
5040 | 1200 | 558 | 0.46 | 586 | 0.56 | 614 | 0.66 | 640 | 0.77 | 664 | 0.87 | 688 | 0.98 | 712 | 1.09 | 758 | 1.31 | 802 | 1.54 | 844 | 1.77
5460 | 1300 | 595 | 0.55 | 622 | 0.65 | 647 | 0.76 | 672 | 0.87 | 696 | 0.99 | 719 | 1.11 | 741 | 1.22 | 784 | 1.46 | 826 | 1.7 | 866 | 1.94
5880 | 1400 | 632 | 0.64 | 658 | 0.76 | 682 | 0.88 | 705 | 0.99 | 728 | 1.12 | 750 | 1.24 | 771 | 1.37 | 812 | 1.62 | 853 | 1.87 | 891 | 2.13
6300 | 1500 | 669 | 0.75 | 694 | 0.88 | 718 | 1 | 740 | 1.13 | 761 | 1.26 | 783 | 1.39 | 803 | 1.52 | 842 | 1.79 | 880 | 2.06 | 917 | 2.33
5720 | 1600 | 707 | 0.87 | 731 | 1.02 | 754 | 1.14 | 775 | 1.28 | 795 | 1.41 | 816 | 1.55 | 835 | 1.69 | 873 | 1.98 | 909 | 2.26 | 944 | 2.55
7140 | 1700 | 745 | 1.01 | 768 | 1.16 | 790 | 1.3 | 811 | 1.44 | 830 | 1.58 | 849 | 1.73 | 868 | 1.87 | 905 | 2.17 | 940 | 2.48 | 973 | 2.78
7560 | 1800 | 784 | 1.16 | 806 | 1.32 | 827 | 1.47 | 847 | 1.62 | 866 | 1.77 | 884 | 1.92 | 902 | 2.07 | 938 | 2.38 | 971 | 2.71 | 1004 | 3.03
7980 | 1900 | 822 | 1.32 | 843 | 1.49 | 864 | 1.66 | 883 | 1.82 | 901 | 1.97 | 919 | 2.13 | 936 | 2.29 | 970 | 2.61 | 1004 | 2.95 | 1035 | 3.29
8400 | 2000 | 861 | 1.51 | 881 | 1.68 | 901 | 1.86 | 920 | 2.03 | 937 | 2.19 | 955 | 2.36 | 971 | 2.52 | 1004 | 2.86 | 1036 | 3.21 | 1067 | 3.56
9240 | 2200 | 939 | 1.93 | 958 | 2.12 | 976 | 2.31 | 994 | 2.51 | 1011 | 2.7 | 1027 | 2.87 | 1043 | 3.05 | 1073 | 3.42 | 1102 | 3.79 | 1132 | 4.17
10080 | 2400 | 1018 | 2.42 | 1035 | 2.63 | 1052 | 2.84 | 1069 | 3.05 | 1085 | 3.26 | 1100 | 3.47 | 1115 | 3.67 | 1144 | 4.06 | 1172 | 4.45 | 1199 | 4.86
10920 | 2600 | 1097 | 3 | 1113 | 3.22 | 1129 | 3.45 | 1144 | 3.68 | 1160 | 3.91 | 1174 | 4.14 | 1189 | 4.37 | 1216 | 4.79 | 1243 | 5.21 | 1268 | 5.64
11760 | 2800 | 1176 | 3.67 | 1191 | 3.91 | 1206 | 4.15 | 1221 | 4.39 | 1235 | 4.64 | 1249 | 4.89 | 1263 | 5.14 | 1289 | 5.62 | 1315 | 6.07 | 1339 | 6.53
12600 | 3000 | 1255 | 4.44 | 1270 | 4.7 | 1284 | 4.95 | 1298 | 5.21 | 1312 | 5.47 | 1325 | 5.74 | 1338 | 6 | 1363 | 6.54 | 1388 | 7.03 | 1411 | 7.52
13440 | 3200 | 1335 | 5.32 | 1349 | 5.59 | 1362 | 5.86 | 1375 | 6.13 | 1388 | 6.41 | 1401 | 6.69 | 1413 | 6.97 | 1438 | 7.54 | 1461 | 8.11 | 1484 | 8.62
14280 | 3400 | 1415 | 6.3 | 1428 | 6.59 | 1441 | 6.88 | 1453 | 7.17 | 1466 | 7.46 | 1478 | 7.75 | 1490 | 8.05 | 1513 | 8.65 | 1535 | 9.26 | 1557 | 9.85
15120 | 3600 | 1496 | 7.41 | 1508 | 7.71 | 1520 | 8.01 | 1532 | 8.32 | 1543 | 8.32 | 1555 | 8.94 | 1566 | 9.25 | 1588 | 9.88 | 1610 | 10.52 | 1631 | 11.16
15960 | 3800 | 1576 | 8.64 | 1588 | 8.96 | 1599 | 9.28 | 1610 | 9.6 | 1622 | 9.6 | 1632 | 10.25 | 1643 | 10.58 | 1665 | 11.24 | 1685 | 11.9 | 1706 | 12.58
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
5880 | 1400 | 928 | 2.4 | 1002 | 2.94 | 1087 | 3.58
6300 | 1500 | 953 | 2.61 | 1023 | 3.18 | 1095 | 3.79 | 1173 | 4.48
6720 | 1600 | 980 | 2.84 | 1046 | 3.44 | 1111 | 4.04 | 1181 | 4.72 | 1253 | 5.46
7140 | 1700 | 1007 | 3.09 | 1071 | 3.71 | 1133 | 4.35 | 1193 | 5 | 1261 | 5.74 | 1329 | 6.52 | 1394 | 7.33
7560 | 1800 | 1035 | 3.35 | 1098 | 4 | 1157 | 4.67 | 1216 | 5.35 | 1272 | 6.04 | 1337 | 6.83 | 1401 | 7.66 | 1463 | 8.51
7980 | 1900 | 1066 | 3.63 | 1125 | 4.31 | 1183 | 5.01 | 1238 | 5.72 | 1294 | 6.43 | 1346 | 7.16 | 1409 | 8.01 | 1470 | 8.88 | 1529 | 9.78
8400 | 2000 | 1097 | 3.92 | 1153 | 4.64 | 1210 | 5.36 | 1264 | 6.1 | 1316 | 6.85 | 1368 | 7.6 | 1418 | 8.37 | 1478 | 9.26 | 1537 | 10.18 | 1593 | 11.12
9240 | 2200 | 1160 | 4.56 | 1214 | 5.34 | 1265 | 6.13 | 1317 | 6.93 | 1367 | 7.73 | 1415 | 8.55 | 1463 | 9.37 | 1510 | 10.2 | 1555 | 11.04 | 1608 | 12.01
10080 | 2400 | 1226 | 5.27 | 1278 | 6.12 | 1327 | 6.98 | 1373 | 7.84 | 1421 | 8.7 | 1467 | 9.57 | 1512 | 10.45 | 1555 | 11.35 | 1599 | 12.24 | 1642 | 13.15
10920 | 2600 | 1293 | 6.08 | 1343 | 6.98 | 1390 | 7.9 | 1435 | 8.83 | 1478 | 9.75 | 1521 | 10.69 | 1565 | 11.63 | 1607 | 12.57 | 1648 | 13.53 | 1687 | 14.5
11760 | 2800 | 1363 | 6.99 | 1409 | 7.94 | 1454 | 8.91 | 1498 | 9.9 | 1540 | 10.9 | 1580 | 11.9 | 1619 | 12.91 | 1661 | 13.91 | 1700 | 14.92 | 1739 | 15.94
12600 | 3000 | 1434 | 8 | 1477 | 9 | 1520 | 10.03 | 1562 | 11.07 | 1603 | 12.13 | 1642 | 13.2 | 1680 | 14.27 | 1717 | 15.34 | 1754 | 16.42 | 1792 | 17.49
13440 | 3200 | 1506 | 9.14 | 1548 | 10.19 | 1588 | 11.26 | 1628 | 12.35 | 1667 | 13.47 | 1705 | 14.6 | 1742 | 15.74 | 1778 | 16.87 | 1813 | 18.01 | 1747 | 19.17
14280 | 3400 | 1578 | 10.39 | 1619 | 11.5 | 1658 | 12.62 | 1695 | 13.76 | 1733 | 14.92 | 1770 | 16.11 | 1806 | 17.31 | 1840 | 18.52 | 1874 | 19.72 | 1907 | 20.92
15120 | 3600 | 1651 | 11.78 | 1691 | 12.93 | 1728 | 14.11 | 1764 | 15.3 | 1799 | 16.51 | 1835 | 17.74 | 1870 | 18.99 | 1904 | 20.26 | 1937 | 21.54 | 1969 | 22.82
15960 | 3800 | 1725 | 13.26 | 1763 | 14.5 | 1800 | 15.73 | 1835 | 16.98 | 1869 | 18.24 | 1902 | 19.52 | 1936 | 20.82 | 1969 | 22.14 | 2001 | 23.47 | 2032 | 24.82
16800 | 4000 | 1800 | 14.84 | 1837 | 16.22 | 1872 | 17.5 | 1906 | 18.8 | 1939 | 20.11 | 1971 | 21.44 | 2002 | 22.79 | 2034 | 24.16 | 2066 | 25.54 | 2096 | 26.94
17640 | 4200 | 1875 | 16.56 | 1910 | 18.06 | 1944 | 19.42 | 1977 | 20.77 | 2009 | 22.14 | 2040 | 23.52 | 2071 | 24.92 | 2100 | 26.33 | 2131 | 27.76 | 2161 | 29.21
18480 | 4400 | 1950 | 18.43 | 1984 | 19.99 | 2018 | 21.51 | 2050 | 22.91 | 2081 | 24.33 | 2111 | 25.76 | 2140 | 27.21 | 2169 | 28.67 | 2197 | 30.14 | 2227 | 31.64
19320 | 4600 | 2026 | 20.46 | 2059 | 22.08 | 2092 | 23.72 | 2123 | 25.21 | 2153 | 26.68 | 2182 | 28.17 | 2211 | 29.66 | 2239 | 31.17 | 2266 | 32.7 | 2293 | 34.24
20160 | 4800 | 2102 | 22.64 | 2134 | 24.32 | 2166 | 26.02 | 2196 | 27.68 | 2225 | 29.21 | 2254 | 30.75 | 2282 | 32.3 | 2309 | 33.86 | 2336 | 35.43 | 2362 | 37.02
21000 | 5000 | 2178 | 25 | 2210 | 26.74 | 2240 | 28.5 | 2270 | 30.28 | 2299 | 31.92 | 2326 | 33.51 | 2354 | 35.11 | 2380 | 36.72 | 2406 | 38.35 | 2432 | 39.99
21840 | 5200 | 2255 | 27.52 | 2285 | 29.33 | 2315 | 31.15 | 2344 | 32.99 | 2372 | 34.82 | 2399 | 36.46 | 2426 | 38.11 | 2452 | 39.78 | 2477 | 41.46 | 2502 | 43.15
22680 | 5400 | 2332 | 30.24 | 2362 | 32.10 | 2390 | 33.98 | 2418 | 35.88 | 2446 | 37.80 | 2473 | 39.61 | 2498 | 41.31 | 2524 | 43.03 | 2549 | 44.76 | 2573 | 46.50
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
10080 | 2400 | 1683 | 14.06 | 1780 | 16.15 | 1876 | 18.36 | 1966 | 20.62
10920 | 2600 | 1728 | 15.47 | 1806 | 17.43 | 1891 | 19.6 | 1982 | 21.97 | 2068 | 24.38
11760 | 2800 | 1776 | 16.97 | 1851 | 19.05 | 1924 | 21.16 | 1997 | 23.35 | 2083 | 25.88 | 2165 | 28.44 | 2244 | 31.05
12600 | 3000 | 1826 | 18.57 | 1900 | 20.77 | 1969 | 23 | 2038 | 25.24 | 2104 | 27.51 | 2181 | 30.09 | 2259 | 32.8 | 2335 | 35.56 | 2407 | 38.35
13440 | 3200 | 1883 | 20.3 | 1952 | 22.6 | 2018 | 24.94 | 2082 | 27.31 | 2148 | 29.69 | 2211 | 32.09 | 2275 | 34.6 | 2350 | 37.47 | 2423 | 40.37 | 2493 | 43.3
14280 | 3400 | 1940 | 22.14 | 2006 | 24.57 | 2071 | 27.01 | 2133 | 29.48 | 2193 | 32 | 2255 | 34.51 | 2315 | 37.04 | 2373 | 39.6 | 2438 | 42.43 | 2508 | 45.47
15120 | 3600 | 2001 | 24.08 | 2062 | 26.65 | 2125 | 29.21 | 2186 | 31.79 | 2245 | 34.4 | 2302 | 37.05 | 2359 | 39.7 | 2417 | 42.36 | 2472 | 45.05 | 2526 | 47.76
15960 | 3800 | 2063 | 26.17 | 2123 | 28.84 | 2180 | 31.55 | 2239 | 34.24 | 2298 | 36.96 | 2354 | 39.7 | 2408 | 42.48 | 2461 | 45.27 | 2517 | 48.07 | 2570 | 50.88
16800 | 4000 | 2126 | 28.35 | 2184 | 31.18 | 2241 | 33.99 | 2295 | 36.84 | 2351 | 39.67 | 2407 | 42.51 | 2460 | 45.39 | 2512 | 48.29 | 2562 | 51.23 | 2614 | 54.15
17640 | 4200 | 2190 | 30.7 | 2247 | 33.63 | 2302 | 36.58 | 2355 | 3954 | 2406 | 42.53 | 2460 | 45.49 | 2513 | 48.46 | 2564 | 51.47 | 2614 | 54.5 | 2663 | 57.56
18480 | 4400 | 2255 | 33.15 | 2311 | 36.21 | 2364 | 39.32 | 2416 | 42.4 | 2467 | 45.49 | 2516 | 48.62 | 2567 | 51.71 | 2618 | 54.82 | 2667 | 57.95 | 2715 | 61.1
19320 | 4600 | 2321 | 35.8 | 2376 | 38.96 | 2428 | 42.17 | 2479 | 45.42 | 2528 | 48.62 | 2576 | 51.85 | 2623 | 55.11 | 2671 | 58.35 | 2720 | 61.57 | 2767 | 64.83
20160 | 4800 | 2388 | 38.62 | 2441 | 41.88 | 2492 | 45.19 | 2842 | 48.54 | 2590 | 51.94 | 2637 | 55.26 | 2683 | 58.62 | 2728 | 62.01 | 2774 | 65.39
21000 | 5000 | 2457 | 41.64 | 2507 | 44.99 | 2557 | 48.4 | 2606 | 51.85 | 2653 | 55.34 | 2699 | 58.87 | 2745 | 62.32 | 2789 | 65.8