## Sheet1
Recommended Tahvieh Hamoon NO FAN TOWER Selections for Common Conditions
95˚ Water On - 85˚ Water Off - 78˚ Entering Wet Bulb Temperature
UNIT CAPACITY |  | SELECTION |  | UNIT CAPACITY |  | SELECTION
Norminal | in | Model | Spray Pressure | Norminal | in | Model | Spray Pressure
Tons | U.S. GPM | Number | PSI | Tons | U.S. GPM | Number | PSI
5 | 15 | T0203-H20 | 22 | 175 | 525 | T0909-H24 | 54
7½ | 22½ | T0203-H23 | 35 |  |  | T1209-H22 | 38
10 | 30 | T0203-H25 | 50 | 190 | 570 | T0909-H25 | 57
|  | T0303-H22 | 25 |  |  | T1209-H22 | 45
15 | 45 | T0303-H25 | 40 | 200 | 600 | T1209-H23 | 45
|  | T0305-H21 | 23 |  |  | T1809-H20 | 28
20 | 60 | T0303-H28 | 58 | 225 | 675 | T1209-H24 | 51
|  | T0305-H23 | 32 |  |  | T1809-H21 | 31
25 | 75 | T0305-B25 | 40 | 250 | 750 | T1209-H25 | 57
|  | T0405-H22 | 22 |  |  | T1809-H21 | 39
30 | 90 | T0305-H27 | 50 | 275 | 825 | T1809-H22 | 41
|  | T0405-H23 | 28 |  |  | T1812-H21 | 26
35 | 105 | T0405-H24 | 34 | 300 | 900 | T1809-H23 | 44
|  | T0605-H21 | 22 |  |  | T1812-H22 | 28
40 | 120 | T0405-H25 | 40 | 325 | 975 | T1809-H23 | 52
|  | T0605-H23 | 30 |  |  | T1812-H22 | 33
45 | 135 | T0405-H26 | 47 | 350 | 1050 | T1809-H24 | 54
|  | T0605-H24 | 30 |  |  | T1812-H23 | 33
50 | 150 | T0405-H27 | 55 | 375 | 1125 | T1809-H25 | 57
|  | T0605-H24 | 32 |  |  | T1812-H23 | 38
60 | 180 | T0605-H25 | 43 | 400 | 1200 | T1812-H24 | 40
|  | T0905-H22 | 25 |  |  | T2412-H22 | 29
70 | 210 | T0605-H27 | 50 | 425 | 1275 | T1812-H24 | 45
|  | T0905-H23 | 31 |  |  | T2412-H22 | 32
75 | 225 | T0605-H27 | 57 | 450 | 1350 | T1812-H25 | 45
|  | T0905-H24 | 32 |  |  | T2412-H23 | 32
80 | 240 | T0605-H29 | 60 | 475 | 1425 | T1812-H25 | 50
|  | T0905-H24 | 36 |  |  | T2412-H23 | 35
90 | 270 | T0905-H25 | 42 | 500 | 1500 | T1812-T25 | 56
|  | T1205-H23 | 30 |  |  | T2412-H23 | 40
100 | 300 | T0905-T26 | 47 | 525 | 1575 | T1812-H26 | 55
|  | T1205-H24 | 33 |  |  | T2412-H24 | 39
110 | 330 | T0905-H27 | 54 | 550 | 1650 | T1812-H27 | 59
|  | T1205-H24 | 40 |  |  | T2412-H24 | 43
125 | 375 | T1205-H25 | 46 | 575 | 1725 | T2412-H25 | 42
|  | T0909-H22 | 34 | 600 | 1800 | T2412-H25 | 47
140 | 420 | T1205-H27 | 50 | 650 | 1950 | T2412-H26 | 50
|  | T0909-H22 | 42 | 700 | 2100 | T2412-H27 | 55
150 | 450 | T1205-H28 | 55 | 750 | 2250 | T2412-H28 | 60
|  | T0909-H23 | 44
160 | 480 | T1205-H29 | 60
|  | T0909-H23 | 50